## Sheet1
21 Commerce Drive
Danbury, CT 06810
Phone: (203) 445-9991
www.accutrolllc.com
AccuValve® Airflow Control Valves
Technology that saves your facility important energy dollars
Project Name
Accutrol Energy Analysis and Comparison
System Data | [5 empty] | Fan Information
|  |  | Supply | Exhaust |  | Avg Fan Efficiency |  | 60%
Peak Airflow (CFM) |  |  | 300000 | 330000 |  | Avg Motor Efficiency |  | 90%
Diversity |  |  | 75% | 75% |  | Annual Operating Hours |  | 8760
Average Airflow (CFM) |  |  | 225000 | 247500 |  | Electric Rate |  | 0.15
|  |  | AccuValve |  | Venturi Valve |  | Savings
|  |  | Supply | Exhaust | Supply | Exhaust | Supply | Exhaust
System Pressure ("wc)
| w/o Valve |  | 5.5 | 3.5 | 5.5 | 3.5
| Valve |  | 0.25 | 0.25 | 1.25 | 1.25
Total System Pressure ('wc) |  |  | 5.75 | 3.75 | 6.75 | 4.75 | 1 | 1
| Motor BHP |  | 339.2464 | 243.3724 | 398.2458 | 308.2717 | 58.9994 | 64.8993
| Electrical Input (kW) |  | 281.1976 | 201.7287 | 330.1015 | 255.523 | 48.9039 | 53.7943
| Annual Energy Usage (kWh) |  | 2463290.5916 | 1767143.2505 | 2891688.9553 | 2238381.4506 | 428398.3638 | 471238.2001
| Annual Energy Cost) |  | 369493.5887 | 265071.4876 | 433753.3433 | 335757.2176 | 64259.7546 | 70685.73
Total Savings (Supply + Exhaust)
|  | Timeframe |  | kWH | Monetary | Percent
|  | Annual |  | 899636.5639 | 134945.4846 | 17.54%
|  | 10 | Years | 8996365.6388 | 1349454.8458
|  | 20 | Years | 17992731.2775 | 2698909.6916
AccuValve operates on significantly lower Pressure
The AccuValve is an electronically pressure independent valve that does not rely on system pressure to maintain its pressure independence. Therefore the fan system can be set to operate at significantly lower pressures than required for a mechanical venturi valve.
AccuValve provides "ready" Demand Based Static Pressure Reset Control
Actual pressure savings will depend upon the settings of the fan pressure setpoint. Maximum savings will be achieved by utilizing demand based static pressure reset control as described in ASHRAE 90.1.6.5.2.3 which can be achieved with no additional equipment when using the AccuValve.
AccuValve allows additional savings on capital equipment cost
Calculations above do not take into consideration reduced capital equipment costs associated with reduced fan and motor BHP requirements.
NOTE: Highlighted cells may be changed by user
ACCUVALVE significantly reduces building energy consumption.
The award winning AccuValve provides its users with substantial energy savings over competitive airflow products used in Universities, Healthcare and Research facilities. The design incorporates low pressure drop operation along with many other technological advantages which makes it a choice product for sustainable “green” buildings.
Energy Saving Features and Benefits
 Low Pressure Drop
· Demand based static pressure
Applications
· Laboratories / Fume Hoods
· Clean Rooms
· Vivarium
· Life Science / Support Spaces
· Healthcare
· Patient Rooms / Isolation Rooms
· No Maintenance Required
can be implemented with no additional equipment
Operating Suites / Pharmacy